## Outflow components
Emitter coefficient, actual demand estimation
Use this sheet to separate base demands into actual base demands and emitter coefficients; to prepare pressure-dependent leakage models in InfoWater
|  | Percentage actual demand = | 85%
|  | Percentage leakage = | 15%
|  | Emitter exponent = | 0.5
Junction ID | Base demand (gpm) | Pressure at noon (psi) | Actual demand (gpm) | Leak flow (gpm) | Emitter coefficient
J10 | 0.15 | 96.871 | 0.1275 | 0.0225 | 0.002286
J12 | 0 | 100.856 | 0 | 0 | 0
J14 | 0 | 107.063 | 0 | 0 | 0
J16 | 0 | 62.329 | 0 | 0 | 0
J18 | 1.14 | 61.648 | 0.969 | 0.171 | 0.021779
J20 | 0.48 | 65.709 | 0.408 | 0.072 | 0.0088822
J22 | 0.15 | 76.383 | 0.1275 | 0.0225 | 0.0025744
J24 | 1.14 | 84.399 | 0.969 | 0.171 | 0.018613
J26 | 1.22 | 84.327 | 1.037 | 0.183 | 0.019928
J28 | 1.64 | 86.339 | 1.394 | 0.246 | 0.026475
J30 | 0.16 | 86.214 | 0.136 | 0.024 | 0.0025848
J32 | 1.45 | 88.17 | 1.2325 | 0.2175 | 0.023163
J34 | 1.3 | 90.657 | 1.105 | 0.195 | 0.02048
J36 | 0.94 | 96.43 | 0.799 | 0.141 | 0.014359
J38 | 0.88 | 101.167 | 0.748 | 0.132 | 0.013124
J40 | 0 | 103.661 | 0 | 0 | 0
J42 | 0.17 | 99.822 | 0.1445 | 0.0255 | 0.0025523
J44 | 0.19 | 102.936 | 0.1615 | 0.0285 | 0.0028091
J46 | 0.19 | 99.848 | 0.1615 | 0.0285 | 0.0028522
J48 | 0.22 | 102.279 | 0.187 | 0.033 | 0.003263
J50 | 0.22 | 96.574 | 0.187 | 0.033 | 0.003358
J52 | 1.1 | 95.421 | 0.935 | 0.165 | 0.016891
J54 | 0.24 | 87.189 | 0.204 | 0.036 | 0.0038554
J56 | 0.24 | 90.948 | 0.204 | 0.036 | 0.0037749
J58 | 0.24 | 74.068 | 0.204 | 0.036 | 0.004183
J60 | 0.25 | 89.228 | 0.2125 | 0.0375 | 0.0039699
J62 | 0.26 | 83.67 | 0.221 | 0.039 | 0.0042636
J64 | 0.28 | 89.638 | 0.238 | 0.042 | 0.0044361
J66 | 1.44 | 81.249 | 1.224 | 0.216 | 0.023963
J68 | 0.3 | 100.99 | 0.255 | 0.045 | 0.0044779
J70 | 2.08 | 99.727 | 1.768 | 0.312 | 0.031243
J72 | 0.15 | 89.86 | 0.1275 | 0.0225 | 0.0023736
J74 | 0.31 | 97.478 | 0.2635 | 0.0465 | 0.0047098
J76 | 0.31 | 92.979 | 0.2635 | 0.0465 | 0.0048224
J78 | 0.32 | 95.729 | 0.272 | 0.048 | 0.0049059
J80 | 0.33 | 78.256 | 0.2805 | 0.0495 | 0.0055956
J82 | 1.18 | 81.669 | 1.003 | 0.177 | 0.019586
J84 | 0.33 | 74.187 | 0.2805 | 0.0495 | 0.005747
J86 | 0.34 | 76.324 | 0.289 | 0.051 | 0.0058377
J88 | 0.34 | 85.231 | 0.289 | 0.051 | 0.0055242
J90 | 0.19 | 108.965 | 0.1615 | 0.0285 | 0.0027302
J92 | 0.66 | 110.455 | 0.561 | 0.099 | 0.0094198
J94 | 1 | 96.536 | 0.85 | 0.15 | 0.015267
J96 | 2.04 | 89.242 | 1.734 | 0.306 | 0.032392
J98 | 1.77 | 92.374 | 1.5045 | 0.2655 | 0.027624
J100 | 3.33 | 91.856 | 2.8305 | 0.4995 | 0.052117
J102 | 2.44 | 91.665 | 2.074 | 0.366 | 0.038228
J104 | 1.99 | 92.172 | 1.6915 | 0.2985 | 0.031092
J106 | 5.56 | 89.902 | 4.726 | 0.834 | 0.087959
J108 | 0.48 | 89.806 | 0.408 | 0.072 | 0.0075977
J110 | 0.84 | 95.386 | 0.714 | 0.126 | 0.012901
J112 | 0.39 | 95.128 | 0.3315 | 0.0585 | 0.0059979
J114 | 0.5 | 73.268 | 0.425 | 0.075 | 0.008762
J116 | 3.4 | 81.695 | 2.89 | 0.51 | 0.056425
J118 | 1.4 | 86.662 | 1.19 | 0.21 | 0.022558
J120 | 0.7 | 90.767 | 0.595 | 0.105 | 0.011021
J122 | 2.3 | 83.635 | 1.955 | 0.345 | 0.037725
J124 | 1.77 | 91.142 | 1.5045 | 0.2655 | 0.02781
J126 | 0.32 | 105.859 | 0.272 | 0.048 | 0.0046653
J128 | 0.32 | 104.307 | 0.272 | 0.048 | 0.0046999
J130 | 0 | 103.346 | 0 | 0 | 0
J132 | 0.21 | 70.432 | 0.1785 | 0.0315 | 0.0037534
J134 | 1.01 | 68.508 | 0.8585 | 0.1515 | 0.018304
J136 | 0.33 | 78.951 | 0.2805 | 0.0495 | 0.0055709
J138 | 0.78 | 84.08 | 0.663 | 0.117 | 0.01276
J140 | 2.4 | 89.968 | 2.04 | 0.36 | 0.037954
J142 | 0.68 | 88.432 | 0.578 | 0.102 | 0.010847
J144 | 2.78 | 85.908 | 2.363 | 0.417 | 0.04499
J146 | 4.15 | 83.524 | 3.5275 | 0.6225 | 0.068114
J148 | 1.37 | 87.183 | 1.1645 | 0.2055 | 0.022009
J150 | 2.43 | 90.761 | 2.0655 | 0.3645 | 0.03826
J152 | 1.05 | 92.363 | 0.8925 | 0.1575 | 0.016388
J154 | 0.32 | 100.027 | 0.272 | 0.048 | 0.0047994
J156 | 0.35 | 107.014 | 0.2975 | 0.0525 | 0.005075
J158 | 0.32 | 125.213 | 0.272 | 0.048 | 0.0042896
J160 | 0.35 | 133.046 | 0.2975 | 0.0525 | 0.0045515
J162 | 0.36 | 97.97 | 0.306 | 0.054 | 0.0054557
J164 | 0.37 | 81.668 | 0.3145 | 0.0555 | 0.0061414
J166 | 1.71 | 88.83 | 1.4535 | 0.2565 | 0.027215
J168 | 0.37 | 107.369 | 0.3145 | 0.0555 | 0.0053562
J170 | 0.29 | 110.501 | 0.2465 | 0.0435 | 0.0041381
J172 | 0.35 | 113.813 | 0.2975 | 0.0525 | 0.0049211
J174 | 1.42 | 110.089 | 1.207 | 0.213 | 0.020301
J176 | 0.27 | 105.43 | 0.2295 | 0.0405 | 0.0039443
J178 | 0.3 | 111.163 | 0.255 | 0.045 | 0.0042681
J180 | 0.37 | 118.936 | 0.3145 | 0.0555 | 0.005089
J182 | 0.78 | 96.045 | 0.663 | 0.117 | 0.011938
J184 | 0.6 | 106.673 | 0.51 | 0.09 | 0.008714
J186 | 0.77 | 110.707 | 0.6545 | 0.1155 | 0.010977
J188 | 1.3 | 74.186 | 1.105 | 0.195 | 0.02264
J190 | 0.55 | 79.647 | 0.4675 | 0.0825 | 0.0092442
J192 | 1.26 | 88.656 | 1.071 | 0.189 | 0.020073
J194 | 1.04 | 96.867 | 0.884 | 0.156 | 0.01585
J196 | 0.36 | 99.697 | 0.306 | 0.054 | 0.0054082
J198 | 0.59 | 76.315 | 0.5015 | 0.0885 | 0.010131
J200 | 0.86 | 84.441 | 0.731 | 0.129 | 0.014038
J202 | 1.13 | 85.538 | 0.9605 | 0.1695 | 0.018327
J204 | 0.68 | 93.285 | 0.578 | 0.102 | 0.010561
J206 | 0.39 | 98.107 | 0.3315 | 0.0585 | 0.0059062
J208 | 0.6 | 103.909 | 0.51 | 0.09 | 0.0088291
J210 | 1.43 | 108.513 | 1.2155 | 0.2145 | 0.020591
J212 | 0.85 | 111.245 | 0.7225 | 0.1275 | 0.012088
J214 | 0.14 | 109.23 | 0.119 | 0.021 | 0.0020093
J216 | 0.66 | 110.114 | 0.561 | 0.099 | 0.0094344
J218 | 0.29 | 113.814 | 0.2465 | 0.0435 | 0.0040775
J220 | 0.4 | 81.089 | 0.34 | 0.06 | 0.006663
J222 | 1.83 | 73.328 | 1.5555 | 0.2745 | 0.032056
J224 | 0.39 | 99.466 | 0.3315 | 0.0585 | 0.0058657
J226 | 0.3 | 109.889 | 0.255 | 0.045 | 0.0042927
J228 | 0.4 | 108.602 | 0.34 | 0.06 | 0.0057575
J230 | 0.4 | 85.433 | 0.34 | 0.06 | 0.0064914
J232 | 0.4 | 75.557 | 0.34 | 0.06 | 0.0069026
J234 | 0.31 | 84.311 | 0.2635 | 0.0465 | 0.0050642
J236 | 0.48 | 81.783 | 0.408 | 0.072 | 0.0079616
J238 | 0.74 | 86.046 | 0.629 | 0.111 | 0.011966
J240 | 1.16 | 88.675 | 0.986 | 0.174 | 0.018478
J242 | 0.89 | 110.976 | 0.7565 | 0.1335 | 0.012673
J244 | 1.14 | 92.662 | 0.969 | 0.171 | 0.017764
J246 | 0.96 | 88.346 | 0.816 | 0.144 | 0.01532
J248 | 1.91 | 104.717 | 1.6235 | 0.2865 | 0.027997
J250 | 0.9 | 99.511 | 0.765 | 0.135 | 0.013533
J252 | 2.06 | 102.877 | 1.751 | 0.309 | 0.030465
J254 | 0.59 | 101.343 | 0.5015 | 0.0885 | 0.0087912
J256 | 1.71 | 88.369 | 1.4535 | 0.2565 | 0.027286
J258 | 0.23 | 90.093 | 0.1955 | 0.0345 | 0.0036347
J260 | 0.31 | 92.286 | 0.2635 | 0.0465 | 0.0048404
J262 | 0.48 | 91.213 | 0.408 | 0.072 | 0.0075388
J264 | 0.64 | 91.714 | 0.544 | 0.096 | 0.010024
J266 | 0.49 | 103.99 | 0.4165 | 0.0735 | 0.0072076
J268 | 0.4 | 116.624 | 0.34 | 0.06 | 0.0055559
J270 | 0.42 | 122.194 | 0.357 | 0.063 | 0.0056992
J272 | 0.43 | 129.226 | 0.3655 | 0.0645 | 0.0056739
J274 | 0.43 | 129.81 | 0.3655 | 0.0645 | 0.0056612
J276 | 0.45 | 130.316 | 0.3825 | 0.0675 | 0.005913
J278 | 1.74 | 125.697 | 1.479 | 0.261 | 0.02328
J280 | 0.54 | 84.569 | 0.459 | 0.081 | 0.008808
J282 | 0.46 | 94.856 | 0.391 | 0.069 | 0.0070846
J284 | 0.28 | 95.306 | 0.238 | 0.042 | 0.0043022
J286 | 0.41 | 106.235 | 0.3485 | 0.0615 | 0.0059668
J288 | 0.61 | 107.659 | 0.5185 | 0.0915 | 0.0088185
J290 | 0.46 | 111.452 | 0.391 | 0.069 | 0.0065359
J292 | 0.46 | 122.106 | 0.391 | 0.069 | 0.0062443
J294 | 0.5 | 126.408 | 0.425 | 0.075 | 0.0066707
J296 | 0.65 | 100.834 | 0.5525 | 0.0975 | 0.0097096
J298 | 0.86 | 58.707 | 0.731 | 0.129 | 0.016836
J300 | 1.75 | 62.841 | 1.4875 | 0.2625 | 0.033114
J302 | 0.66 | 64.394 | 0.561 | 0.099 | 0.012337
J304 | 0.71 | 73.317 | 0.6035 | 0.1065 | 0.012438
J306 | 0.85 | 90.186 | 0.7225 | 0.1275 | 0.013426
J308 | 0.5 | 66.652 | 0.425 | 0.075 | 0.0091866
J310 | 0.62 | 68.069 | 0.527 | 0.093 | 0.011272
J312 | 1.43 | 65.583 | 1.2155 | 0.2145 | 0.026487
J314 | 0.62 | 72.005 | 0.527 | 0.093 | 0.01096
J316 | 0.62 | 76.693 | 0.527 | 0.093 | 0.01062
J318 | 0.63 | 78.199 | 0.5355 | 0.0945 | 0.010686
J320 | 0.64 | 97.12 | 0.544 | 0.096 | 0.0097413
J322 | 0.69 | 112.63 | 0.5865 | 0.1035 | 0.0097524
J324 | 0.7 | 125.442 | 0.595 | 0.105 | 0.0093749
J326 | 0.6 | 114.088 | 0.51 | 0.09 | 0.008426
J328 | 1.38 | 102.566 | 1.173 | 0.207 | 0.020439
J330 | 1.14 | 107.842 | 0.969 | 0.171 | 0.016467
J332 | 0.75 | 116.105 | 0.6375 | 0.1125 | 0.010441
J334 | 0.39 | 71.072 | 0.3315 | 0.0585 | 0.0069392
J336 | 0 | 108.691 | 0 | 0 | 0
J338 | 0 | 99.076 | 0 | 0 | 0
J340 | 0 | 101.499 | 0 | 0 | 0
J342 | 0 | 124.423 | 0 | 0 | 0
J344 | 0 | 144.476 | 0 | 0 | 0
J346 | 0.76 | 157.508 | 0.646 | 0.114 | 0.0090835
J348 | 0.76 | 103.412 | 0.646 | 0.114 | 0.01121
J350 | 0.76 | 109.748 | 0.646 | 0.114 | 0.010882
J352 | 0.43 | 69.295 | 0.3655 | 0.0645 | 0.0077483
J354 | 0.33 | 77.473 | 0.2805 | 0.0495 | 0.0056238
J356 | 0.36 | 75.746 | 0.306 | 0.054 | 0.0062046
J358 | 1 | 76.092 | 0.85 | 0.15 | 0.017196
J360 | 0.19 | 73.988 | 0.1615 | 0.0285 | 0.0033133
J362 | 1.36 | 67.638 | 1.156 | 0.204 | 0.024805
J364 | 0.28 | 89.273 | 0.238 | 0.042 | 0.0044452
J366 | 0.41 | 89.953 | 0.3485 | 0.0615 | 0.0064844
J368 | 0.65 | 100.259 | 0.5525 | 0.0975 | 0.0097374
J370 | 0.86 | 106.494 | 0.731 | 0.129 | 0.0125
J372 | 1.38 | 74.275 | 1.173 | 0.207 | 0.024019
J374 | 1.14 | 59.694 | 0.969 | 0.171 | 0.022133
J376 | 0.39 | 68.38 | 0.3315 | 0.0585 | 0.0070744
J378 | 0.48 | 71.139 | 0.408 | 0.072 | 0.0085365
J380 | 0.39 | 54.054 | 0.3315 | 0.0585 | 0.0079569
J382 | 1.08 | 74.97 | 0.918 | 0.162 | 0.01871
J384 | 0.21 | 75.652 | 0.1785 | 0.0315 | 0.0036216
J386 | 1.15 | 70.634 | 0.9775 | 0.1725 | 0.020525
J388 | 0.31 | 89.361 | 0.2635 | 0.0465 | 0.004919
J390 | 0.74 | 99.668 | 0.629 | 0.111 | 0.011118
J392 | 0.75 | 60.932 | 0.6375 | 0.1125 | 0.014412
J394 | 0.98 | 77.113 | 0.833 | 0.147 | 0.01674
J396 | 0.99 | 56.558 | 0.8415 | 0.1485 | 0.019746
J398 | 0.76 | 62.809 | 0.646 | 0.114 | 0.014384
J400 | 0.83 | 68.724 | 0.7055 | 0.1245 | 0.015018
J402 | 1.64 | 81.723 | 1.394 | 0.246 | 0.027212
J404 | 0.69 | 99.77 | 0.5865 | 0.1035 | 0.010362
J406 | 1.31 | 86.053 | 1.1135 | 0.1965 | 0.021183
J408 | 1.59 | 76.338 | 1.3515 | 0.2385 | 0.027297
J410 | 0.45 | 90.866 | 0.3825 | 0.0675 | 0.0070811
J412 | 1.43 | 92.511 | 1.2155 | 0.2145 | 0.022301
J414 | 0.68 | 99.339 | 0.578 | 0.102 | 0.010234
J416 | 0.29 | 97.282 | 0.2465 | 0.0435 | 0.0044103
J418 | 1.44 | 108.991 | 1.224 | 0.216 | 0.02069
J420 | 0.79 | 95.268 | 0.6715 | 0.1185 | 0.012141
J422 | 0.81 | 99.115 | 0.6885 | 0.1215 | 0.012204
J424 | 0.81 | 100.337 | 0.6885 | 0.1215 | 0.01213
J426 | 0.82 | 101.457 | 0.697 | 0.123 | 0.012211
J428 | 0.82 | 103.591 | 0.697 | 0.123 | 0.012085
J430 | 0.84 | 97.719 | 0.714 | 0.126 | 0.012746
J432 | 0.84 | 64.113 | 0.714 | 0.126 | 0.015736
J434 | 0.84 | 62.336 | 0.714 | 0.126 | 0.015959
J436 | 25 | 58.839 | 21.25 | 3.75 | 0.48888
J438 | 0.87 | 74.511 | 0.7395 | 0.1305 | 0.015118
J440 | 0.87 | 66.672 | 0.7395 | 0.1305 | 0.015982
J442 | 0.87 | 82.111 | 0.7395 | 0.1305 | 0.014402
J444 | 0.89 | 89.451 | 0.7565 | 0.1335 | 0.014115
J446 | 0.9 | 93.94 | 0.765 | 0.135 | 0.013929
J448 | 0.91 | 86.866 | 0.7735 | 0.1365 | 0.014646
J450 | 0.91 | 76.007 | 0.7735 | 0.1365 | 0.015657
J452 | 0.93 | 92.163 | 0.7905 | 0.1395 | 0.014531
J454 | 0.96 | 82.427 | 0.816 | 0.144 | 0.015861
J456 | 0.93 | 75.538 | 0.7905 | 0.1395 | 0.016051
J458 | 0.97 | 104.033 | 0.8245 | 0.1455 | 0.014265
J460 | 0.97 | 103.395 | 0.8245 | 0.1455 | 0.014309
J462 | 0.98 | 104.414 | 0.833 | 0.147 | 0.014386
J464 | 0.98 | 99.391 | 0.833 | 0.147 | 0.014745
J466 | 1 | 101.587 | 0.85 | 0.15 | 0.014882
J468 | 1.09 | 92.613 | 0.9265 | 0.1635 | 0.01699
J470 | 1 | 82.905 | 0.85 | 0.15 | 0.016474
J472 | 1.06 | 78.673 | 0.901 | 0.159 | 0.017926
J474 | 1.07 | 75.508 | 0.9095 | 0.1605 | 0.01847
J476 | 1.08 | 69.734 | 0.918 | 0.162 | 0.0194
J478 | 1.08 | 66.013 | 0.918 | 0.162 | 0.019939
J480 | 1.09 | 74.431 | 0.9265 | 0.1635 | 0.018951
J482 | 1.09 | 72.489 | 0.9265 | 0.1635 | 0.019204
J484 | 1.12 | 84.685 | 0.952 | 0.168 | 0.018256
J486 | 1.12 | 84.99 | 0.952 | 0.168 | 0.018223
J488 | 1.12 | 89.318 | 0.952 | 0.168 | 0.017776
J490 | 1.13 | 96.476 | 0.9605 | 0.1695 | 0.017257
J492 | 1.16 | 95.844 | 0.986 | 0.174 | 0.017773
J494 | 1.17 | 95.279 | 0.9945 | 0.1755 | 0.01798
J496 | 1.19 | 75.855 | 1.0115 | 0.1785 | 0.020495
J498 | 1.19 | 78.24 | 1.0115 | 0.1785 | 0.02018
J500 | 1.22 | 83.32 | 1.037 | 0.183 | 0.020048
J502 | 1.25 | 89.17 | 1.0625 | 0.1875 | 0.019856
J504 | 1.27 | 82.505 | 1.0795 | 0.1905 | 0.020973
J506 | 1.28 | 82.332 | 1.088 | 0.192 | 0.02116
J508 | 1.28 | 92.232 | 1.088 | 0.192 | 0.019992
J510 | 1.29 | 100.982 | 1.0965 | 0.1935 | 0.019256
J512 | 1.33 | 109.79 | 1.1305 | 0.1995 | 0.01904
J514 | 1.38 | 65.505 | 1.173 | 0.207 | 0.025576
J516 | 1.4 | 66.437 | 1.19 | 0.21 | 0.025764
J518 | 1.4 | 80.415 | 1.19 | 0.21 | 0.023418
J520 | 1.44 | 90.672 | 1.224 | 0.216 | 0.022684
J522 | 1.45 | 93.628 | 1.2325 | 0.2175 | 0.022478
J524 | 1.45 | 96.191 | 1.2325 | 0.2175 | 0.022176
J526 | 1.45 | 85.984 | 1.2325 | 0.2175 | 0.023456
J528 | 1.45 | 88.058 | 1.2325 | 0.2175 | 0.023178
J530 | 1.45 | 90.927 | 1.2325 | 0.2175 | 0.022809
J532 | 1.45 | 98.06 | 1.2325 | 0.2175 | 0.021964
J534 | 1.45 | 100.533 | 1.2325 | 0.2175 | 0.021692
J536 | 1.46 | 99.33 | 1.241 | 0.219 | 0.021974
J538 | 1.48 | 72.629 | 1.258 | 0.222 | 0.026049
J540 | 1.55 | 74.886 | 1.3175 | 0.2325 | 0.026867
J542 | 1.57 | 77.525 | 1.3345 | 0.2355 | 0.026747
J544 | 1.61 | 79.419 | 1.3685 | 0.2415 | 0.027099
J546 | 1.27 | 81.64 | 1.0795 | 0.1905 | 0.021084
J548 | 1.28 | 83.551 | 1.088 | 0.192 | 0.021005
J550 | 1.28 | 86.64 | 1.088 | 0.192 | 0.020627
J552 | 1.29 | 89.81 | 1.0965 | 0.1935 | 0.020418
J554 | 1.38 | 91.74 | 1.173 | 0.207 | 0.021612
J556 | 1.33 | 79.447 | 1.1305 | 0.1995 | 0.022382
J558 | 1.34 | 82.155 | 1.139 | 0.201 | 0.022176
J560 | 1.35 | 74.645 | 1.1475 | 0.2025 | 0.023438
J562 | 1.35 | 77.388 | 1.1475 | 0.2025 | 0.023019
J564 | 1.39 | 90.79 | 1.1815 | 0.2085 | 0.021882
J566 | 1.4 | 85.773 | 1.19 | 0.21 | 0.022675
J568 | 1.4 | 84.539 | 1.19 | 0.21 | 0.02284
J570 | 1.4 | 85.791 | 1.19 | 0.21 | 0.022672
J572 | 1.41 | 90.877 | 1.1985 | 0.2115 | 0.022186
J574 | 0.12 | 93.773 | 0.102 | 0.018 | 0.0018588
J576 | 0.12 | 92.55 | 0.102 | 0.018 | 0.001871
J578 | 0.28 | 109.869 | 0.238 | 0.042 | 0.0040069
J580 | 0.88 | 86.947 | 0.748 | 0.132 | 0.014156
J582 | 0.17 | 68.201 | 0.1445 | 0.0255 | 0.0030878
J584 | 50 | 79.88 | 42.5 | 7.5 | 0.83916
J586 | 0.18 | 80.87 | 0.153 | 0.027 | 0.0030024
J588 | 0.18 | 93.19 | 0.153 | 0.027 | 0.0027969
J590 | 0.2 | 108.353 | 0.17 | 0.03 | 0.002882
J592 | 0.2 | 108.175 | 0.17 | 0.03 | 0.0028844
J594 | 0.77 | 72.106 | 0.6545 | 0.1155 | 0.013602
J596 | 0.77 | 80.683 | 0.6545 | 0.1155 | 0.012859
J598 | 0.21 | 103.105 | 0.1785 | 0.0315 | 0.0031022
J600 | 0.2 | 100.943 | 0.17 | 0.03 | 0.002986
J602 | 10.2 | 84.041 | 8.67 | 1.53 | 0.1669
J604 | 0.5 | 84.892 | 0.425 | 0.075 | 0.0081401
J606 | 0.26 | 78.455 | 0.221 | 0.039 | 0.0044031
J608 | 0.27 | 80.399 | 0.2295 | 0.0405 | 0.0045168
J610 | 0.27 | 96.157 | 0.2295 | 0.0405 | 0.0041301
J612 | 0.28 | 103.891 | 0.238 | 0.042 | 0.0041206
J614 | 0.28 | 109.868 | 0.238 | 0.042 | 0.0040069
J616 | 0.28 | 42.359 | 0.238 | 0.042 | 0.0064532
J618 | 0.28 | 50.064 | 0.238 | 0.042 | 0.0059359
J620 | 0.3 | 52.393 | 0.255 | 0.045 | 0.0062169
J622 | 0.3 | 64.245 | 0.255 | 0.045 | 0.0056143
J624 | 0.31 | 68.903 | 0.2635 | 0.0465 | 0.0056019
J626 | 0.31 | 81.018 | 0.2635 | 0.0465 | 0.0051661
J628 | 0.31 | 95.588 | 0.2635 | 0.0465 | 0.0047561
J630 | 0.31 | 89.366 | 0.2635 | 0.0465 | 0.0049189
J632 | 0.32 | 89.404 | 0.272 | 0.048 | 0.0050765
J634 | 0.36 | 76.185 | 0.306 | 0.054 | 0.0061867
J636 | 0.34 | 67.07 | 0.289 | 0.051 | 0.0062274
J638 | 0.36 | 83.992 | 0.306 | 0.054 | 0.0058922
J640 | 0.36 | 92.036 | 0.306 | 0.054 | 0.0056288
J642 | 0.37 | 97.44 | 0.3145 | 0.0555 | 0.0056224
J644 | 0.38 | 40.602 | 0.323 | 0.057 | 0.0089454
J646 | 0.38 | 40.925 | 0.323 | 0.057 | 0.0089101
J648 | 0.38 | 47.084 | 0.323 | 0.057 | 0.0083069
J650 | 0.38 | 82.47 | 0.323 | 0.057 | 0.0062766
J652 | 0.38 | 102.646 | 0.323 | 0.057 | 0.0056261
J654 | 0.39 | 107.684 | 0.3315 | 0.0585 | 0.0056374
J656 | 0.41 | 126.974 | 0.3485 | 0.0615 | 0.0054578
J658 | 0.41 | 94.327 | 0.3485 | 0.0615 | 0.0063322
J660 | 0.43 | 93.225 | 0.3655 | 0.0645 | 0.0066803
J662 | 0.43 | 98.74 | 0.3655 | 0.0645 | 0.006491
J664 | 0.43 | 103.148 | 0.3655 | 0.0645 | 0.0063508
J666 | 0.43 | 100.177 | 0.3655 | 0.0645 | 0.0064443
J668 | 0.82 | 98.137 | 0.697 | 0.123 | 0.012416
J670 | 0.82 | 107.899 | 0.697 | 0.123 | 0.011841
J672 | 0.82 | 102.756 | 0.697 | 0.123 | 0.012134
J674 | 0.82 | 65.84 | 0.697 | 0.123 | 0.015159
J676 | 0.82 | 74.002 | 0.697 | 0.123 | 0.014298
J678 | 0.85 | 63.023 | 0.7225 | 0.1275 | 0.016061
J680 | 0.99 | 65.722 | 0.8415 | 0.1485 | 0.018318
J682 | 0.86 | 60.96 | 0.731 | 0.129 | 0.016522
J684 | 0.92 | 49.95 | 0.782 | 0.138 | 0.019526
J686 | 1.05 | 73.885 | 0.8925 | 0.1575 | 0.018323
J688 | 0.95 | 66.784 | 0.8075 | 0.1425 | 0.017437
J690 | 1.02 | 70.31 | 0.867 | 0.153 | 0.018247
J692 | 1.02 | 80.235 | 0.867 | 0.153 | 0.017081
J694 | 1.9 | 84.527 | 1.615 | 0.285 | 0.030999
J696 | 1.05 | 89.522 | 0.8925 | 0.1575 | 0.016646
J698 | 1.02 | 86.89 | 0.867 | 0.153 | 0.016414
J700 | 1.05 | 95.284 | 0.8925 | 0.1575 | 0.016135
J702 | 1.11 | 72.811 | 0.9435 | 0.1665 | 0.019513
J704 | 1.11 | 69.792 | 0.9435 | 0.1665 | 0.01993
J706 | 1.12 | 66.944 | 0.952 | 0.168 | 0.020533
J708 | 2.2 | 92.961 | 1.87 | 0.33 | 0.034227
J710 | 6.88 | 95.608 | 5.848 | 1.032 | 0.10554
J712 | 1.71 | 96.595 | 1.4535 | 0.2565 | 0.026098
J714 | 1.72 | 98.455 | 1.462 | 0.258 | 0.026002
J716 | 0 | 101.99 | 0 | 0 | 0
J718 | 0 | 103.86 | 0 | 0 | 0
J720 | 3.6 | 91.261 | 3.06 | 0.54 | 0.056526
J722 | 1.1 | 89.011 | 0.935 | 0.165 | 0.017489
J724 | 1.1 | 85.249 | 0.935 | 0.165 | 0.017871
J726 | 1.7 | 85.856 | 1.445 | 0.255 | 0.02752
J728 | 0.27 | 88.012 | 0.2295 | 0.0405 | 0.004317
J730 | 0.36 | 87.938 | 0.306 | 0.054 | 0.0057584
J732 | 0.94 | 81.745 | 0.799 | 0.141 | 0.015595
J734 | 0.88 | 83.786 | 0.748 | 0.132 | 0.014421
J736 | 4.22 | 84.32 | 3.587 | 0.633 | 0.068935
J738 | 0 | 98.203 | 0 | 0 | 0
J740 | 0.78 | 100.338 | 0.663 | 0.117 | 0.01168
J742 | 2.2 | 84.693 | 1.87 | 0.33 | 0.035858
J744 | 0.44 | 90.57 | 0.374 | 0.066 | 0.0069351
J746 | 0 | 90.846 | 0 | 0 | 0
J748 | 0.22 | 92.407 | 0.187 | 0.033 | 0.0034329
J750 | 0 | 90.558 | 0 | 0 | 0
J752 | 0 | 91.86 | 0 | 0 | 0
J754 | 0.13 | 93.499 | 0.1105 | 0.0195 | 0.0020167
J756 | 0.45 | 93.096 | 0.3825 | 0.0675 | 0.0069958
J758 | 0.64 | 92.762 | 0.544 | 0.096 | 0.0099675
J760 | 2.64 | 85.663 | 2.244 | 0.396 | 0.042786
J762 | 4.58 | 90.647 | 3.893 | 0.687 | 0.072157
J764 | 3.62 | 91.677 | 3.077 | 0.543 | 0.056711
J766 | 0.88 | 91.371 | 0.748 | 0.132 | 0.013809
J768 | 0 | 86.11 | 0 | 0 | 0
J770 | 2.1 | 83.844 | 1.785 | 0.315 | 0.034401
J772 | 2.29 | 83.045 | 1.9465 | 0.3435 | 0.037694
J774 | 3.11 | 83.987 | 2.6435 | 0.4665 | 0.050903
J776 | 2.77 | 86.263 | 2.3545 | 0.4155 | 0.044736
J778 | 2.79 | 86.146 | 2.3715 | 0.4185 | 0.04509
J780 | 3.37 | 85.868 | 2.8645 | 0.5055 | 0.054551
J782 | 2.14 | 81.66 | 1.819 | 0.321 | 0.035522
J784 | 1.88 | 81.723 | 1.598 | 0.282 | 0.031194
J786 | 1.14 | 51.161 | 0.969 | 0.171 | 0.023907
J788 | 1.12 | 54.728 | 0.952 | 0.168 | 0.022709
J790 | 1.14 | 47.392 | 0.969 | 0.171 | 0.02484
J792 | 1.14 | 61.397 | 0.969 | 0.171 | 0.021823
J794 | 1.18 | 74.217 | 1.003 | 0.177 | 0.020546
J796 | 1.18 | 39.397 | 1.003 | 0.177 | 0.0282
J798 | 1.18 | 46.718 | 1.003 | 0.177 | 0.025896
J800 | 0.96 | 62.1 | 0.816 | 0.144 | 0.018273
J802 | 0.98 | 61.248 | 0.833 | 0.147 | 0.018783
J804 | 0.55 | 52.442 | 0.4675 | 0.0825 | 0.011392
J806 | 0.57 | 69.424 | 0.4845 | 0.0855 | 0.010262
J808 | 0.57 | 89.133 | 0.4845 | 0.0855 | 0.0090562
J810 | 0.58 | 72.102 | 0.493 | 0.087 | 0.010246
J812 | 0.59 | 86.461 | 0.5015 | 0.0885 | 0.0095177
J814 | 0.59 | 94.585 | 0.5015 | 0.0885 | 0.0090998
J816 | 0.59 | 85.344 | 0.5015 | 0.0885 | 0.0095798
J818 | 0.59 | 84.078 | 0.5015 | 0.0885 | 0.0096517
J820 | 0.6 | 97.94 | 0.51 | 0.09 | 0.0090942
J822 | 6.7 | 71.488 | 5.695 | 1.005 | 0.11886
J824 | 1.28 | 69.302 | 1.088 | 0.192 | 0.023064
J826 | 5.8 | 66.097 | 4.93 | 0.87 | 0.10701
J828 | 0.65 | 95.193 | 0.5525 | 0.0975 | 0.0099931
J830 | 0.65 | 94.185 | 0.5525 | 0.0975 | 0.010046
J832 | 0.66 | 97.948 | 0.561 | 0.099 | 0.010003
J834 | 0.66 | 94.275 | 0.561 | 0.099 | 0.010196
J836 | 0.66 | 93.062 | 0.561 | 0.099 | 0.010262
J838 | 0.68 | 97.533 | 0.578 | 0.102 | 0.010328
J840 | 0.68 | 102.28 | 0.578 | 0.102 | 0.010086
J842 | 0.68 | 92.899 | 0.578 | 0.102 | 0.010583
J844 | 0.69 | 97.687 | 0.5865 | 0.1035 | 0.010472
J846 | 0.7 | 101.516 | 0.595 | 0.105 | 0.010421
J848 | 0.7 | 104.386 | 0.595 | 0.105 | 0.010277
J850 | 0.72 | 96.122 | 0.612 | 0.108 | 0.011016
J852 | 0.72 | 60.233 | 0.612 | 0.108 | 0.013916
J854 | 0.74 | 63.72 | 0.629 | 0.111 | 0.013905
J856 | 0.76 | 66.274 | 0.646 | 0.114 | 0.014003
J858 | 0.77 | 88.782 | 0.6545 | 0.1155 | 0.012258
J860 | 0.77 | 59.453 | 0.6545 | 0.1155 | 0.014979
J862 | 0.8 | 85.241 | 0.68 | 0.12 | 0.012997
J864 | 0.84 | 86.662 | 0.714 | 0.126 | 0.013535
J866 | 0.14 | 79.21 | 0.119 | 0.021 | 0.0023596
J868 | 0.84 | 84.008 | 0.714 | 0.126 | 0.013747
J870 | 0.84 | 75.174 | 0.714 | 0.126 | 0.014532
J872 | 0.87 | 77.153 | 0.7395 | 0.1305 | 0.014857
J874 | 0.88 | 81.31 | 0.748 | 0.132 | 0.014639
J876 | 0.88 | 84.151 | 0.748 | 0.132 | 0.014389
J878 | 0.88 | 76.848 | 0.748 | 0.132 | 0.015058
J880 | 0.88 | 91.977 | 0.748 | 0.132 | 0.013764
J882 | 0.88 | 85.274 | 0.748 | 0.132 | 0.014294
J884 | 0.88 | 78.674 | 0.748 | 0.132 | 0.014882
J886 | 0.85 | 79.513 | 0.7225 | 0.1275 | 0.014299
J888 | 1.71 | 85.084 | 1.4535 | 0.2565 | 0.027808
J890 | 0.85 | 82.281 | 0.7225 | 0.1275 | 0.014056
J892 | 1.96 | 82.934 | 1.666 | 0.294 | 0.032284
J894 | 0.89 | 76.274 | 0.7565 | 0.1335 | 0.015286
J896 | 1.94 | 85.833 | 1.649 | 0.291 | 0.03141
J898 | 0.91 | 67.554 | 0.7735 | 0.1365 | 0.016608
J900 | 0.92 | 74.431 | 0.782 | 0.138 | 0.015996
J902 | 0.94 | 80.357 | 0.799 | 0.141 | 0.015729
J904 | 0.95 | 82.704 | 0.8075 | 0.1425 | 0.015669
J906 | 0.95 | 89.697 | 0.8075 | 0.1425 | 0.015046
J908 | 0.96 | 96.252 | 0.816 | 0.144 | 0.014678
J910 | 1 | 109.304 | 0.85 | 0.15 | 0.014347
J912 | 1.01 | 109.51 | 0.8585 | 0.1515 | 0.014477
J914 | 1.01 | 106.029 | 0.8585 | 0.1515 | 0.014713
J916 | 1.4 | 102.874 | 1.19 | 0.21 | 0.020705
J918 | 1.42 | 104.375 | 1.207 | 0.213 | 0.020849
J920 | 1.43 | 107.155 | 1.2155 | 0.2145 | 0.020721
J922 | 1.44 | 87.339 | 1.224 | 0.216 | 0.023113
J924 | 1.44 | 86.082 | 1.224 | 0.216 | 0.023281
J926 | 1.45 | 77.702 | 1.2325 | 0.2175 | 0.024674
J928 | 1.46 | 80.106 | 1.241 | 0.219 | 0.024469
J930 | 0.12 | 99.594 | 0.102 | 0.018 | 0.0018037
J932 | 0.12 | 95.883 | 0.102 | 0.018 | 0.0018382
J934 | 0.14 | 92.971 | 0.119 | 0.021 | 0.0021779
J936 | 0.17 | 86.444 | 0.1445 | 0.0255 | 0.0027427
J938 | 0.17 | 90.886 | 0.1445 | 0.0255 | 0.0026748
J940 | 0.2 | 90.387 | 0.17 | 0.03 | 0.0031555
J942 | 0.21 | 76.187 | 0.1785 | 0.0315 | 0.0036089
J944 | 0.22 | 96.581 | 0.187 | 0.033 | 0.0033579
J946 | 0.22 | 86.1 | 0.187 | 0.033 | 0.0035564
J948 | 0.29 | 91.132 | 0.2465 | 0.0435 | 0.0045567
J950 | 0.22 | 99.288 | 0.187 | 0.033 | 0.0033118
J952 | 0.23 | 100.959 | 0.1955 | 0.0345 | 0.0034336
J954 | 0.24 | 105.735 | 0.204 | 0.036 | 0.003501
J956 | 0.27 | 81.193 | 0.2295 | 0.0405 | 0.0044946
J958 | 0.28 | 86.248 | 0.238 | 0.042 | 0.0045225
J960 | 0.29 | 91.665 | 0.2465 | 0.0435 | 0.0045435
J962 | 0.3 | 92.682 | 0.255 | 0.045 | 0.0046743
J964 | 0.3 | 98.436 | 0.255 | 0.045 | 0.0045356
J966 | 0.3 | 95.417 | 0.255 | 0.045 | 0.0046068
J968 | 0.3 | 89.084 | 0.255 | 0.045 | 0.0047677
J970 | 0.3 | 98.131 | 0.255 | 0.045 | 0.0045427
J972 | 0.32 | 84.11 | 0.272 | 0.048 | 0.0052338
J974 | 0.32 | 83.381 | 0.272 | 0.048 | 0.0052566
J976 | 0.33 | 85.366 | 0.2805 | 0.0495 | 0.0053575
J978 | 0.33 | 92.306 | 0.2805 | 0.0495 | 0.0051522
J980 | 0.33 | 92.11 | 0.2805 | 0.0495 | 0.0051576
J982 | 0.33 | 91.293 | 0.2805 | 0.0495 | 0.0051807
J984 | 0.35 | 90.671 | 0.2975 | 0.0525 | 0.0055135
J986 | 0.38 | 90.067 | 0.323 | 0.057 | 0.0060061
J988 | 0.39 | 89.805 | 0.3315 | 0.0585 | 0.0061731
J990 | 0.39 | 89.706 | 0.3315 | 0.0585 | 0.0061765
J992 | 0.39 | 89.774 | 0.3315 | 0.0585 | 0.0061742
J994 | 0.4 | 90.676 | 0.34 | 0.06 | 0.0063009
J996 | 0.41 | 94.79 | 0.3485 | 0.0615 | 0.0063168
J998 | 0.41 | 96.846 | 0.3485 | 0.0615 | 0.0062493
J1000 | 0.41 | 89.079 | 0.3485 | 0.0615 | 0.0065161
J1002 | 0.41 | 90.848 | 0.3485 | 0.0615 | 0.0064523
J1004 | 0.41 | 108.291 | 0.3485 | 0.0615 | 0.0059099
J1006 | 0.43 | 109.928 | 0.3655 | 0.0645 | 0.0061518
J1008 | 0.44 | 60.947 | 0.374 | 0.066 | 0.0084541
J1012 | 2.07 | 61.154 | 1.7595 | 0.3105 | 0.039705
J1014 | 0.44 | 82.474 | 0.374 | 0.066 | 0.0072675
J1016 | 0.46 | 94.387 | 0.391 | 0.069 | 0.0071022
J1018 | 0.47 | 97.095 | 0.3995 | 0.0705 | 0.0071547
J1020 | 0.47 | 105.249 | 0.3995 | 0.0705 | 0.006872
J1022 | 0.47 | 93.736 | 0.3995 | 0.0705 | 0.0072818
J1024 | 0.51 | 90.112 | 0.4335 | 0.0765 | 0.0080588
J1026 | 0.51 | 88.655 | 0.4335 | 0.0765 | 0.0081247
J1028 | 0.51 | 88.198 | 0.4335 | 0.0765 | 0.0081458
J1030 | 0.51 | 92.036 | 0.4335 | 0.0765 | 0.0079741
J1032 | 0.51 | 94.356 | 0.4335 | 0.0765 | 0.0078755
J1034 | 0.52 | 105.808 | 0.442 | 0.078 | 0.0075829
J1036 | 0.53 | 93.747 | 0.4505 | 0.0795 | 0.0082109
J1038 | 0.57 | 93.507 | 0.4845 | 0.0855 | 0.0088419
J1040 | 0.58 | 87.64 | 0.493 | 0.087 | 0.0092933
J1042 | 0.63 | 97.8 | 0.5355 | 0.0945 | 0.0095557
J1044 | 0.63 | 84.436 | 0.5355 | 0.0945 | 0.010284
J1046 | 0.63 | 78.596 | 0.5355 | 0.0945 | 0.010659
J1048 | 0.6 | 85.701 | 0.51 | 0.09 | 0.0097219
J1050 | 0.56 | 76.425 | 0.476 | 0.084 | 0.0096086
J1052 | 0.56 | 84.676 | 0.476 | 0.084 | 0.0091285
J1054 | 0.56 | 93.053 | 0.476 | 0.084 | 0.0087079
J1056 | 0.56 | 101.458 | 0.476 | 0.084 | 0.0083394
J1058 | 0.6 | 97.232 | 0.51 | 0.09 | 0.0091272
J1060 | 0.61 | 68.223 | 0.5185 | 0.0915 | 0.011078
J1062 | 0.61 | 82.362 | 0.5185 | 0.0915 | 0.010082
J1064 | 0.62 | 94.463 | 0.527 | 0.093 | 0.0095687
J1066 | 0.62 | 88.225 | 0.527 | 0.093 | 0.0099012
J1068 | 0.62 | 82.312 | 0.527 | 0.093 | 0.010251
J1070 | 0.64 | 80.36 | 0.544 | 0.096 | 0.010709
J1072 | 0.64 | 63.137 | 0.544 | 0.096 | 0.012082
J1074 | 1.96 | 61.594 | 1.666 | 0.294 | 0.037461
J1076 | 0.64 | 95.339 | 0.544 | 0.096 | 0.0098319
J1078 | 0.64 | 81.142 | 0.544 | 0.096 | 0.010657
J1080 | 0.65 | 90.989 | 0.5525 | 0.0975 | 0.010221
J1082 | 0.66 | 80.495 | 0.561 | 0.099 | 0.011034
J1084 | 0.7 | 77.673 | 0.595 | 0.105 | 0.011914
J1086 | 0.66 | 77.541 | 0.561 | 0.099 | 0.011243
J1088 | 0.7 | 88.994 | 0.595 | 0.105 | 0.01113
J1090 | 0.7 | 83.215 | 0.595 | 0.105 | 0.01151
J1092 | 0.71 | 84.589 | 0.6035 | 0.1065 | 0.01158
J1094 | 0.71 | 84.562 | 0.6035 | 0.1065 | 0.011581
J1096 | 0.71 | 81.448 | 0.6035 | 0.1065 | 0.011801
J1098 | 0.71 | 87.026 | 0.6035 | 0.1065 | 0.011416
J1100 | 0.73 | 84.859 | 0.6205 | 0.1095 | 0.011887
J1102 | 0.73 | 84.248 | 0.6205 | 0.1095 | 0.01193
J1104 | 0.78 | 88.235 | 0.663 | 0.117 | 0.012456
J1106 | 0.79 | 87.15 | 0.6715 | 0.1185 | 0.012694
J1108 | 0.79 | 91.515 | 0.6715 | 0.1185 | 0.012387
J1110 | 0.8 | 82.943 | 0.68 | 0.12 | 0.013176
J1112 | 0.8 | 84.322 | 0.68 | 0.12 | 0.013068
J1114 | 0.79 | 85.214 | 0.6715 | 0.1185 | 0.012837
J1116 | 0.8 | 90.172 | 0.68 | 0.12 | 0.012637
J1118 | 0.83 | 78.298 | 0.7055 | 0.1245 | 0.01407
J1120 | 0.83 | 80.324 | 0.7055 | 0.1245 | 0.013891
J1122 | 0.83 | 81.433 | 0.7055 | 0.1245 | 0.013797
J1124 | 0.84 | 83.11 | 0.714 | 0.126 | 0.013821
J1126 | 0.84 | 84.298 | 0.714 | 0.126 | 0.013723
J1128 | 0.85 | 81.606 | 0.7225 | 0.1275 | 0.014114
J1130 | 0.88 | 80.358 | 0.748 | 0.132 | 0.014725
J1132 | 0.88 | 67.577 | 0.748 | 0.132 | 0.016057
J1134 | 0.9 | 83.281 | 0.765 | 0.135 | 0.014793
J1136 | 0.92 | 78.285 | 0.782 | 0.138 | 0.015597
J1138 | 0.93 | 77.957 | 0.7905 | 0.1395 | 0.0158
J1140 | 0.94 | 74.35 | 0.799 | 0.141 | 0.016352
J1142 | 0.11 | 82.105 | 0.0935 | 0.0165 | 0.001821
J1144 | 0.11 | 80.371 | 0.0935 | 0.0165 | 0.0018405
J1146 | 0.13 | 65.332 | 0.1105 | 0.0195 | 0.0024125
J1148 | 0.16 | 66.402 | 0.136 | 0.024 | 0.0029452
J1150 | 0.14 | 52.878 | 0.119 | 0.021 | 0.0028879
J1152 | 1.97 | 66.391 | 1.6745 | 0.2955 | 0.036266
J1154 | 0.18 | 65.039 | 0.153 | 0.027 | 0.0033479
J1156 | 0.18 | 57.9 | 0.153 | 0.027 | 0.0035483
J1158 | 0.19 | 72.85 | 0.1615 | 0.0285 | 0.0033391
J1160 | 0.19 | 79.51 | 0.1615 | 0.0285 | 0.0031962
J1162 | 0.19 | 59.886 | 0.1615 | 0.0285 | 0.0036828
J1164 | 0.2 | 65.885 | 0.17 | 0.03 | 0.003696
J1166 | 0.21 | 71.437 | 0.1785 | 0.0315 | 0.0037269
J1168 | 0.26 | 79.254 | 0.221 | 0.039 | 0.0043808
J1170 | 0.24 | 77.748 | 0.204 | 0.036 | 0.0040828
J1172 | 0.25 | 72.867 | 0.2125 | 0.0375 | 0.004393
J1174 | 0.26 | 66.987 | 0.221 | 0.039 | 0.0047651
J1176 | 0.26 | 69.557 | 0.221 | 0.039 | 0.0046762
J1178 | 0.26 | 64.938 | 0.221 | 0.039 | 0.0048397
J1180 | 0.26 | 72.745 | 0.221 | 0.039 | 0.0045726
J1182 | 0.26 | 68.007 | 0.221 | 0.039 | 0.0047292
J1184 | 0.28 | 55.89 | 0.238 | 0.042 | 0.005618
J1186 | 0.28 | 67.889 | 0.238 | 0.042 | 0.0050974
J1188 | 0.29 | 74.754 | 0.2465 | 0.0435 | 0.0050312
J1190 | 0.41 | 73.556 | 0.3485 | 0.0615 | 0.0071708
J1192 | 0.29 | 78.161 | 0.2465 | 0.0435 | 0.0049203
J1194 | 0.29 | 84.701 | 0.2465 | 0.0435 | 0.0047266
J1196 | 0.29 | 87.726 | 0.2465 | 0.0435 | 0.0046444
J1198 | 0.31 | 77.17 | 0.2635 | 0.0465 | 0.0052933
J1200 | 0.33 | 79.771 | 0.2805 | 0.0495 | 0.0055422
J1202 | 0.41 | 83.393 | 0.3485 | 0.0615 | 0.0067346
J1204 | 1.71 | 98.076 | 1.4535 | 0.2565 | 0.0259
J1206 | 0.41 | 86.26 | 0.3485 | 0.0615 | 0.0066217
J1208 | 0.44 | 74.474 | 0.374 | 0.066 | 0.0076479
J1210 | 0.45 | 84.438 | 0.3825 | 0.0675 | 0.0073457
J1212 | 0.47 | 81.01 | 0.3995 | 0.0705 | 0.0078328
J1214 | 0.45 | 81.554 | 0.3825 | 0.0675 | 0.0074745
J1216 | 0.45 | 81.437 | 0.3825 | 0.0675 | 0.0074799
J1218 | 0.45 | 75.8 | 0.3825 | 0.0675 | 0.007753
J1220 | 0.45 | 85.667 | 0.3825 | 0.0675 | 0.0072928
J1222 | 0.71 | 82.316 | 0.6035 | 0.1065 | 0.011738
J1224 | 0.48 | 79.55 | 0.408 | 0.072 | 0.0080726
J1226 | 0.55 | 97.692 | 0.4675 | 0.0825 | 0.0083469
J1228 | 0.56 | 77.517 | 0.476 | 0.084 | 0.0095407
J1230 | 0.59 | 72.666 | 0.5015 | 0.0885 | 0.010382
J1232 | 0.79 | 76.034 | 0.6715 | 0.1185 | 0.01359
J1234 | 0.6 | 72.063 | 0.51 | 0.09 | 0.010602
J1236 | 0.81 | 75.604 | 0.6885 | 0.1215 | 0.013973
J1238 | 0.6 | 76.807 | 0.51 | 0.09 | 0.010269
J1240 | 0.84 | 80.022 | 0.714 | 0.126 | 0.014085
J1242 | 0.64 | 86.026 | 0.544 | 0.096 | 0.01035
J1244 | 0.64 | 85.521 | 0.544 | 0.096 | 0.010381
J1246 | 0.64 | 83.039 | 0.544 | 0.096 | 0.010535
J1248 | 0.64 | 82.401 | 0.544 | 0.096 | 0.010576
J1250 | 0.64 | 79.764 | 0.544 | 0.096 | 0.010749
J1252 | 0.65 | 83.675 | 0.5525 | 0.0975 | 0.010659
J1254 | 0.66 | 82.458 | 0.561 | 0.099 | 0.010902
J1256 | 0.73 | 80.157 | 0.6205 | 0.1095 | 0.01223
J1258 | 0.78 | 81.349 | 0.663 | 0.117 | 0.012972
J1260 | 0.78 | 86.393 | 0.663 | 0.117 | 0.012588
J1262 | 0.79 | 79.006 | 0.6715 | 0.1185 | 0.013332
J1264 | 0.79 | 79.988 | 0.6715 | 0.1185 | 0.01325
J1266 | 0.84 | 83.61 | 0.714 | 0.126 | 0.01378
J1268 | 0.86 | 90.627 | 0.731 | 0.129 | 0.013551
J1270 | 0.86 | 94.874 | 0.731 | 0.129 | 0.013244
J1272 | 0.88 | 97.654 | 0.748 | 0.132 | 0.013358
J1274 | 0.88 | 83.803 | 0.748 | 0.132 | 0.014419
J1276 | 0.88 | 87.145 | 0.748 | 0.132 | 0.01414
J1278 | 0.9 | 90.848 | 0.765 | 0.135 | 0.014164
J1280 | 0.9 | 84.812 | 0.765 | 0.135 | 0.014659
J1282 | 0.9 | 88.149 | 0.765 | 0.135 | 0.014379
J1284 | 0.92 | 92.475 | 0.782 | 0.138 | 0.01435
J1286 | 0.93 | 92.56 | 0.7905 | 0.1395 | 0.0145
J1288 | 0.94 | 95.328 | 0.799 | 0.141 | 0.014441
J1290 | 0.94 | 96.735 | 0.799 | 0.141 | 0.014336
J1292 | 0.99 | 98.802 | 0.8415 | 0.1485 | 0.01494
J1294 | 0.99 | 99.863 | 0.8415 | 0.1485 | 0.01486
J1296 | 0.99 | 99.144 | 0.8415 | 0.1485 | 0.014914
J1298 | 1 | 98.066 | 0.85 | 0.15 | 0.015147
J1300 | 1 | 90.598 | 0.85 | 0.15 | 0.015759
J1302 | 1.01 | 82.666 | 0.8585 | 0.1515 | 0.016663
J1304 | 1.01 | 83.234 | 0.8585 | 0.1515 | 0.016606
J1306 | 1.04 | 89.294 | 0.884 | 0.156 | 0.016509
J1308 | 1.04 | 91.289 | 0.884 | 0.156 | 0.016327
J1310 | 1.11 | 93.931 | 0.9435 | 0.1665 | 0.017179
J1312 | 1.13 | 91.415 | 0.9605 | 0.1695 | 0.017728
J1314 | 1.13 | 77.029 | 0.9605 | 0.1695 | 0.019313
J1316 | 1.14 | 77.488 | 0.969 | 0.171 | 0.019426
J1318 | 1.14 | 83.347 | 0.969 | 0.171 | 0.018731
J1320 | 1.14 | 84.16 | 0.969 | 0.171 | 0.01864
J1322 | 1.16 | 91.068 | 0.986 | 0.174 | 0.018233
J1324 | 1.16 | 85.821 | 0.986 | 0.174 | 0.018782
J1326 | 1.16 | 84.946 | 0.986 | 0.174 | 0.018879
J1328 | 1.2 | 84.359 | 1.02 | 0.18 | 0.019598
J1330 | 1.37 | 84.486 | 1.1645 | 0.2055 | 0.022357
J1332 | 1.42 | 86.61 | 1.207 | 0.213 | 0.022887
J1334 | 1.71 | 86.192 | 1.4535 | 0.2565 | 0.027628
J1336 | 1.42 | 91.877 | 1.207 | 0.213 | 0.022222
J1338 | 1.45 | 97.02 | 1.2325 | 0.2175 | 0.022082
J1340 | 1.48 | 99.272 | 1.258 | 0.222 | 0.022281
J1342 | 1.49 | 81.622 | 1.2665 | 0.2235 | 0.024739
J1344 | 1.51 | 86.081 | 1.2835 | 0.2265 | 0.024413
J1346 | 1.51 | 85.098 | 1.2835 | 0.2265 | 0.024553
J1348 | 1.71 | 101.15 | 1.4535 | 0.2565 | 0.025504
J1350 | 1.52 | 100.324 | 1.292 | 0.228 | 0.022763
J1352 | 1.57 | 96.462 | 1.3345 | 0.2355 | 0.023978
J1354 | 0.77 | 95.623 | 0.6545 | 0.1155 | 0.011811
J1356 | 0 | 99.95 | 0 | 0 | 0
J1358 | 1.63 | 87.243 | 1.3855 | 0.2445 | 0.026177
J1360 | 1.65 | 85.996 | 1.4025 | 0.2475 | 0.026689
J1362 | 1.65 | 89.112 | 1.4025 | 0.2475 | 0.026218
J1364 | 1.7 | 90.039 | 1.445 | 0.255 | 0.026874
J1366 | 0 | 88.11 | 0 | 0 | 0
J1368 | 0 | 90.762 | 0 | 0 | 0
J1370 | 1.71 | 83.544 | 1.4535 | 0.2565 | 0.028063
J1372 | 0.76 | 91.71 | 0.646 | 0.114 | 0.011904
J1374 | 1.14 | 90.781 | 0.969 | 0.171 | 0.017947
J1376 | 3.2 | 89.698 | 2.72 | 0.48 | 0.050682
J1378 | 3.4 | 89.465 | 2.89 | 0.51 | 0.053919
J1380 | 5.22 | 86.693 | 4.437 | 0.783 | 0.084095
J1382 | 0 | 68.448 | 0 | 0 | 0
J1384 | 4 | 62.214 | 3.4 | 0.6 | 0.076069
J1386 | 1.29 | 94.387 | 1.0965 | 0.1935 | 0.019917
J1388 | 0.4 | 68.923 | 0.34 | 0.06 | 0.0072272
J1390 | 1.14 | 68.735 | 0.969 | 0.171 | 0.020626
J1392 | 0.71 | 81.618 | 0.6035 | 0.1065 | 0.011788
J1394 | 1.87 | 145.748 | 1.5895 | 0.2805 | 0.023234
J1396 | 0.16 | 51.966 | 0.136 | 0.024 | 0.0033293
J1398 | 0.26 | 67.723 | 0.221 | 0.039 | 0.0047391
J1400 | 2.05 | 80.638 | 1.7425 | 0.3075 | 0.034243
J1404 | 0 | -0.643 | 0 | 0 | 0
J1406 | 0 | 141.636 | 0 | 0 | 0
J1414 | 0 | 73.225 | 0 | 0 | 0
8450 | 0.26 | 48.516 | 0.221 | 0.039 | 0.0055992
8452 | 0.91 | 47.58 | 0.7735 | 0.1365 | 0.019789
8454 | 0.17 | 67.655 | 0.1445 | 0.0255 | 0.0031002
8456 | 0.25 | 74.106 | 0.2125 | 0.0375 | 0.0043562
8458 | 0.38 | 95.447 | 0.323 | 0.057 | 0.0058344
8460 | 0.59 | 96.956 | 0.5015 | 0.0885 | 0.0089879
8462 | 0.17 | 51.816 | 0.1445 | 0.0255 | 0.0035425
8464 | 0.1 | 67.183 | 0.085 | 0.015 | 0.00183
8466 | 1.24 | 88.478 | 1.054 | 0.186 | 0.019774
8468 | 0.13 | 43.705 | 0.1105 | 0.0195 | 0.0029496
8470 | 0.09 | 54.984 | 0.0765 | 0.0135 | 0.0018206
8472 | 0.09 | 68.575 | 0.0765 | 0.0135 | 0.0016302
8474 | 0.1 | 45.382 | 0.085 | 0.015 | 0.0022266
8476 | 1.5 | 95.494 | 1.275 | 0.225 | 0.023025
8478 | 5 | 89.645 | 4.25 | 0.75 | 0.079213
8480 | 3.2 | 88.225 | 2.72 | 0.48 | 0.051103
8482 | 100 | 86.297 | 85 | 15 | 1.6147
8484 |  | 62.849 | 0 | 0 | 0
8486 | 0.25 | 84.347 | 0.2125 | 0.0375 | 0.0040832
8490 |  | 88.945 | 0 | 0 | 0
Note on B8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Take this column's values from your model's Junction Demand Data DB table (Input)
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Select a time in the day with representative pressure and copy the values from the report table (input)
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The portion of the outflow that corresponds to actual demand. Copy these values into the Junction Demand Data DB table. (output)
Note on F8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Solve the emitter coefficient for each node from the emitter equation Q=cp^x. Copy the resulting values in the Junction Emitter DB table under "Extended Modeling Data". (output)

## Demand, leakage results
Actual demand, leak flow time series
Use this sheet to visualize the total outflow, actual demand, and leakage flow in a junction, and to create actual demand patterns
|  | Emitter coefficient = | 0.011078
|  | Emitter exponent = | 0.5
|  | Average = | 0.093589 | 0.5185
Time (h) | Total outflow (gpm) | Pressure (psi) | Emitter flow (gpm) | Actual demand (gpm) | New pattern
0 | 0.38253 | 97.0888 | 0.10915 | 0.27338 | 0.52725
0.25 | 0.34978 | 98.8421 | 0.11014 | 0.23964 | 0.46218
0.5 | 0.32543 | 99.828 | 0.11068 | 0.21475 | 0.41417
0.75 | 0.3171 | 100.1092 | 0.11084 | 0.20626 | 0.39779
1 | 0.30102 | 100.6356 | 0.11113 | 0.18989 | 0.36623
1.25 | 0.30102 | 100.6356 | 0.11113 | 0.18989 | 0.36623
1.5 | 0.30936 | 100.3652 | 0.11098 | 0.19838 | 0.38259
1.75 | 0.30936 | 100.3652 | 0.11098 | 0.19838 | 0.38259
2 | 0.30936 | 100.3652 | 0.11098 | 0.19838 | 0.38259
2.25 | 0.29269 | 100.9003 | 0.11128 | 0.18141 | 0.34987
2.5 | 0.30102 | 100.6356 | 0.11113 | 0.18989 | 0.36623
2.75 | 0.30102 | 100.6356 | 0.11113 | 0.18989 | 0.36623
3 | 0.30102 | 100.6356 | 0.11113 | 0.18989 | 0.36623
3.25 | 0.30936 | 100.3652 | 0.11098 | 0.19838 | 0.38259
3.5 | 0.30102 | 100.6356 | 0.11113 | 0.18989 | 0.36623
3.75 | 0.32543 | 99.8278 | 0.11068 | 0.21475 | 0.41417
4 | 0.3171 | 100.1092 | 0.11084 | 0.20626 | 0.39779
4.25 | 0.32543 | 99.828 | 0.11068 | 0.21475 | 0.41417
4.5 | 0.32543 | 99.828 | 0.11068 | 0.21475 | 0.41417
4.75 | 0.34978 | 98.8429 | 0.11014 | 0.23964 | 0.46218
5 | 0.37419 | 97.5473 | 0.10941 | 0.26478 | 0.51066
5.25 | 0.37419 | 97.5475 | 0.10941 | 0.26478 | 0.51066
5.5 | 0.49273 | 89.7183 | 0.10493 | 0.3878 | 0.74792
5.75 | 0.5296 | 86.3629 | 0.10295 | 0.42665 | 0.82285
6 | 0.61101 | 77.443 | 0.097487 | 0.51353 | 0.99041
6.25 | 0.64786 | 73.3307 | 0.094863 | 0.553 | 1.0665
6.5 | 0.78236 | 55.9236 | 0.082843 | 0.69952 | 1.3491
6.75 | 0.7658 | 58.3266 | 0.084604 | 0.6812 | 1.3138
7 | 0.79831 | 53.5252 | 0.081047 | 0.71727 | 1.3833
7.25 | 0.81037 | 51.0926 | 0.079183 | 0.73119 | 1.4102
7.5 | 0.84257 | 44.2442 | 0.073686 | 0.76888 | 1.4829
7.75 | 0.90854 | 26.3048 | 0.056816 | 0.85173 | 1.6427
8 | 0.84607 | 43.4294 | 0.073004 | 0.77307 | 1.491
8.25 | 0.85424 | 41.6715 | 0.071511 | 0.78272 | 1.5096
8.5 | 0.85017 | 42.5296 | 0.072244 | 0.77793 | 1.5003
8.75 | 0.88549 | 33.0469 | 0.063683 | 0.82181 | 1.585
9 | 0.85008 | 42.4367 | 0.072165 | 0.77791 | 1.5003
9.25 | 0.83847 | 45.0898 | 0.074387 | 0.76409 | 1.4736
9.5 | 0.80631 | 51.8839 | 0.079794 | 0.72651 | 1.4012
9.75 | 0.77408 | 57.1311 | 0.083732 | 0.69035 | 1.3314
10 | 0.79004 | 54.7813 | 0.081992 | 0.70805 | 1.3656
10.25 | 0.81447 | 50.2541 | 0.078531 | 0.73594 | 1.4194
10.5 | 0.76166 | 58.9138 | 0.085028 | 0.67663 | 1.305
10.75 | 0.79004 | 54.7777 | 0.081989 | 0.70805 | 1.3656
11 | 0.77408 | 57.1277 | 0.08373 | 0.69035 | 1.3314
11.25 | 0.81447 | 50.2556 | 0.078532 | 0.73594 | 1.4194
11.5 | 0.7658 | 58.3243 | 0.084602 | 0.6812 | 1.3138
11.75 | 0.78236 | 55.9264 | 0.082845 | 0.69951 | 1.3491
12 | 0.69709 | 67.5292 | 0.091034 | 0.60606 | 1.1689
12.25 | 0.69295 | 68.0429 | 0.091379 | 0.60157 | 1.1602
12.5 | 0.66804 | 71.0468 | 0.093374 | 0.57467 | 1.1083
12.75 | 0.65201 | 72.8574 | 0.094557 | 0.55746 | 1.0751
13 | 0.62768 | 75.5641 | 0.096297 | 0.53138 | 1.0248
13.25 | 0.65617 | 72.3875 | 0.094251 | 0.56192 | 1.0837
13.5 | 0.67219 | 70.5619 | 0.093055 | 0.57913 | 1.1169
13.75 | 0.70895 | 66.0325 | 0.090019 | 0.61893 | 1.1937
14 | 0.68049 | 69.5681 | 0.092398 | 0.58809 | 1.1342
14.25 | 0.62352 | 76.0187 | 0.096586 | 0.52694 | 1.0163
14.5 | 0.63183 | 75.1132 | 0.096009 | 0.53582 | 1.0334
14.75 | 0.65617 | 72.3877 | 0.094251 | 0.56192 | 1.0837
15 | 0.64786 | 73.3275 | 0.094861 | 0.553 | 1.0665
15.25 | 0.63183 | 75.1117 | 0.096008 | 0.53582 | 1.0334
15.5 | 0.63183 | 75.1122 | 0.096009 | 0.53583 | 1.0334
15.75 | 0.61517 | 76.938 | 0.097169 | 0.518 | 0.99904
16 | 0.66449 | 71.4556 | 0.093643 | 0.57084 | 1.1009
16.25 | 0.69294 | 68.049 | 0.091383 | 0.60156 | 1.1602
16.5 | 0.71725 | 64.9607 | 0.089286 | 0.62796 | 1.2111
16.75 | 0.7048 | 66.5572 | 0.090376 | 0.61442 | 1.185
17 | 0.73324 | 62.8448 | 0.087819 | 0.64542 | 1.2448
17.25 | 0.7865 | 55.312 | 0.082388 | 0.70411 | 1.358
17.5 | 0.88591 | 34.0437 | 0.064636 | 0.82127 | 1.5839
17.75 | 0.85016 | 42.57 | 0.072278 | 0.77788 | 1.5002
18 | 0.84257 | 44.2258 | 0.07367 | 0.76889 | 1.4829
18.25 | 0.87804 | 36.2019 | 0.066653 | 0.81139 | 1.5649
18.5 | 0.8262 | 47.7724 | 0.076567 | 0.74963 | 1.4458
18.75 | 0.7658 | 58.3279 | 0.084605 | 0.6812 | 1.3138
19 | 0.75397 | 59.9974 | 0.085807 | 0.66816 | 1.2886
19.25 | 0.76166 | 58.922 | 0.085034 | 0.67663 | 1.305
19.5 | 0.76166 | 58.9195 | 0.085033 | 0.67663 | 1.305
19.75 | 0.70065 | 67.0834 | 0.090733 | 0.60992 | 1.1763
20 | 0.7048 | 66.5632 | 0.09038 | 0.61442 | 1.185
20.25 | 0.70895 | 66.034 | 0.09002 | 0.61893 | 1.1937
20.5 | 0.7048 | 66.556 | 0.090375 | 0.61442 | 1.185
20.75 | 0.66033 | 71.9216 | 0.093948 | 0.56638 | 1.0923
21 | 0.63183 | 75.1113 | 0.096008 | 0.53583 | 1.0334
21.25 | 0.61517 | 76.9378 | 0.097169 | 0.518 | 0.99904
21.5 | 0.66804 | 71.0512 | 0.093377 | 0.57467 | 1.1083
21.75 | 0.57477 | 81.6523 | 0.1001 | 0.47467 | 0.91546
22 | 0.57061 | 82.1237 | 0.10039 | 0.47022 | 0.90688
22.25 | 0.52127 | 87.1542 | 0.10342 | 0.41785 | 0.80589
22.5 | 0.52543 | 86.7613 | 0.10319 | 0.42225 | 0.81437
22.75 | 0.46834 | 91.7094 | 0.10609 | 0.36225 | 0.69866
23 | 0.41948 | 94.9743 | 0.10796 | 0.31153 | 0.60082
23.25 | 0.39505 | 96.3887 | 0.10876 | 0.28629 | 0.55214
23.5 | 0.37419 | 97.5456 | 0.10941 | 0.26478 | 0.51066
23.75 | 0.33794 | 99.3952 | 0.11044 | 0.22749 | 0.43875
24 | 0.38253 | 97.0884 | 0.10915 | 0.27338 | 0.52725
Note on D4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Obrtain this value from the junction (input)
Note on B8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Obtain these values from the demand time series in the Report Manager (input)
Note on C8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Obtain these values from the pressure time series in the Report Manager (input)
Note on D8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Computed using the emitter equation: Q=cp^x (output)
Note on E8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The difference between the total outflow and the emitter flow (output)
Note on F8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Normalized actual demand pattern. Copy these values into a new pattern and assign to corresponding junctions. (output)